Florida Photovoltaic Rebate Program

Acceptance Test Checklist

| Sections 1 and 2 to be completed by Rebate Office from information supplied on application |  |
| --- | --- |
| # General Information |  |
| Customer Name Address Phone Number(s) |  |
| Electric Utility, Contact Individual and Phone Number(s) |  |
| Who to contact for scheduling acceptance test site visit | Customer Utility |
| # System/Equipment Information | (Information from List of Approved Systems) |
| System Approval Case No. |  |
| Manufacturer/Supplier Designation |  |
| Manufacturer, Model and Number of PV Modules |  |
| Nameplate STC Array Rating (W dc) |  |
| Manufacturer, Model and Number of Inverters |  |
| Manufacturer, Model and Number of Batteries |  |
| Other Information: |  |
| Sections 3 through 6 to be completed by evaluator during on-site inspection |  |
| # Equipment and System Verification | Evaluator Entries (below) |
| Is installed equipment consistent with system information supplied with rebate application in Section 2 above? (Check/verify manufacturer, model and number of modules, inverters and batteries) | Yes / No Comments (as applicable): |
| Is owner in possession of approved System Manual associated with the System Approval Case No., and includes all documents listed on System Approval Certificate? | Yes / No Comments (as applicable): |
| # Installation Issues |  |
| Array azimuth orientation and tilt angle: (Measure using compass and inclinometer and record) | Azimuth: E, SE, S, SW, W Tilt: ______ deg |
| Is the array shaded anytime between +/- 3 hours from solar noon at any time of year? If yes, describe extent, direction and estimated effects on system performance, e.g. expected percentage output reduction. Use sun path device as required. | Yes / No |
| Observations on the overall quality and safety of the system installation, including array mounting and weather sealing, electrical code compliance and wiring practice (take photos): | Comments (as applicable): |
| # Performance Verification and System Functionality |  |
| DC Output Measurement (optional) |  |
| Are all PV array source circuits producing expected* current output at given irradiance level? (Refer to module/array specifications and configuration) | Yes / No * Is measured current within 15% of STC-rated Imp x measured kW/m2? Measure with Fluke i1010 DC clamp-on meter |
| AC Output Measurement (required) |  |
| Is AC power output consistent with expectations* for given irradiance level? For battery systems w/ load sub panel, disconnect sub panel loads and measure AC power delivered from inverter to main panel and grid. Disable bulk or float battery charging as applicable. | Yes / No AC Power: _______ watts, Irradiance: _______ kW/m2 * Is measured power output within 65% of STC-rated array power x kW/m2? Measure revolution rate with standard utility watthour meter (if installed), or use Fluke 43 PQ Analyzer or Veris power meter. |
| Overall observations about system performance or functionality: | Comments (as applicable): |
| Metering installed on PV output? If so, record current meter reading identify source of future data, and indicate if FSEC monitoring equipment is installed. | None Customer-supplied Utility-supplied __________ kWh Source of data: Customer / Utility FSEC Monitoring Yes / No Type: ________________________ |
| # Acceptance Test Information |  |
| Date of Acceptance Test |  |
| Name of Evaluator |  |